# Battery Sizing Calculation (48 V System)

## Design Inputs

| Parameter | Value |
| --- | --- |
| Project | Off-Grid Solar PV System |
| Location | Bilhari, Madhya Pradesh, India |
| Daily Energy Consumption | 52.5 kWh/day |
| System Voltage | 48 V |
| Battery Model | DEKA Solar PV 8G8D |
| Battery Type | Sealed Gel Lead Acid |
| Battery Rating | 12 V, 208 Ah |
| Days of Autonomy | 1 Day |
| Depth of Discharge (DoD) | 80% |
| Temperature Correction Factor | 0.90 |

## Step-by-Step Calculations

Step 1: Required Battery Energy = 52.5 × 1 = 52.5 kWh.

Step 2: Corrected Battery Energy = 52.5 ÷ (0.80 × 0.90) = 72.92 kWh.

Step 3: Required Battery Capacity = (72.92 × 1000) ÷ 48 = 1,519 Ah ≈ 1,520 Ah.

Step 4: Batteries in Series = 48 ÷ 12 = 4.

Step 5: Parallel Strings = 1,520 ÷ 208 = 7.31 ≈ 8.

Step 6: Total Batteries = 4 × 8 = 32.

Step 7: Installed Capacity = 208 × 8 = 1,664 Ah.

Step 8: Installed Battery Energy = 48 × 1,664 = 79.87 kWh.

Step 9: Usable Energy @80% DoD = 79.87 × 0.80 = 63.90 kWh.

## Final Battery Bank Configuration

| Item | Result |
| --- | --- |
| Battery Model | DEKA Solar PV 8G8D |
| Battery Type | Sealed Gel Lead Acid |
| Battery Rating | 12 V, 208 Ah |
| System Voltage | 48 V |
| Required Capacity | 1,520 Ah |
| Installed Capacity | 1,664 Ah |
| Batteries in Series | 4 |
| Parallel Strings | 8 |
| Total Batteries | 32 |
| Nominal Battery Energy | 79.87 kWh |
| Usable Battery Energy (80% DoD) | 63.90 kWh |
| Days of Autonomy | 1 Day |
| Temperature Correction Factor | 0.90 |
| Design Status | Acceptable |