# MPPT Charge Controller Sizing

| Parameter | Value |
| --- | --- |
| Project | Off-Grid Solar PV System |
| Location | Bilhari, Madhya Pradesh, India |
| Daily Load | 52.5 kWh/day |
| PV Array Capacity | 15.30 kWp |
| PV Module | LG Electronics LG450 N2W-E6 |
| Module Rating | 450 W |
| Number of Modules | 34 |
| Configuration | 2 Series × 17 Parallel |
| Battery Voltage | 48 V |
| Battery Type | HERE DEKA Solar PV 8G8D Sealed Gel |
| Charge Controller | Victron SmartSolar MPPT 150/100 48V |
| Maximum PV Voltage | 150 V |
| Maximum Charging Current | 100 A |

## Step-by-Step Calculations

Step 1: Total PV Power = 34 × 450 = 15,300 W = 15.30 kWp.

Step 2: Controller Power = 48 V × 100 A = 4,800 W (Victron allows practical PV oversizing to approximately 5.8 kWp).

Step 3: Required Controllers = 15.30 / 5.8 = 2.64 ≈ 3 controllers (minimum theoretical).

Step 4: PVsyst design uses 5 Victron SmartSolar MPPT 150/100 controllers.

Step 5: PV Capacity per Controller = 15.30 / 5 = 3.06 kWp.

Step 6: Operating Current per Controller = 184 / 5 = 36.8 A.

Step 7: Safety Margin = 100 − 36.8 = 63.2 A.

## Final MPPT Configuration

| Item | Result |
| --- | --- |
| Controller Model | Victron SmartSolar MPPT 150/100 48V |
| Maximum PV Voltage | 150 V |
| Maximum Charging Current | 100 A |
| Battery Voltage | 48 V |
| Total PV Capacity | 15.30 kWp |
| Number of Controllers | 5 |
| PV Capacity per Controller | 3.06 kWp |
| Operating Current per Controller | 36.8 A |
| Safety Margin | 63.2 A |
| Controller Status | Adequately Sized |